## Input-Output
INPUT | [6 empty] | OUTPUT
PROCESS DATA | [6 empty] | OTR CALCULATIONS
1• Insert influent data in the green cells:
Plant flow | 25 | MGD
| 94500 | m3/d
PE bCOD | 250 | mgCOD/l |  | HRT | 8.8 | h | Plant Load | 85106.2004 | lbO2/day
PE NH4-N | 40 | mgCOD/l |  | Tank volume | 9.1667 | MG |  | 38638.215 | kgO2/day
SE bCOD | 10 | mgCOD/l |  |  | 34650 | m3 | O2 required (OTRreq) | 63430.87 | lbO2/day
SE NH4-N | 1 | mgCOD/l |  | MLSS | 1400 | mg/l |  | 28797.615 | kgO2/day
Mean Cell Retention Time | 7 | days |  | biomass | 106850.2203 | lb
Wasting rate | 15264.3172 | lbMLSS/d |  |  | 48510 | kg
| 6930 | kgMLSS/d |  |  |  |  | DESIGN VALUES
2• Insert in the yellow cell a code from the table below:
Diffuser Code | Diffuser |  | Area |  | min AFR | max AFR
|  |  | ft2 | m2 | SCFM/diff | SCFM/diff | Air Flow Rate | 16508.5284 | SCFM
Diffuser Code | Diffuser |  | Area |  | min | max |  | 467.4695 | Sm3air / min
1 | 7” Ceramic Dome |  | 0.47146 | 0.0438 | 0.5 | 3 | diffusers required | 33018
2 | 7” EPDM Membrane Disc |  | 0.17115 | 0.0159 | 0.5 | 1.7 | normalized air flux | 0.11774 | Sft3air / ftdepth*ft2tot diff area*min
3 | 7” Plastic Disc |  | 0.26587 | 0.0247 | 0.5 | 2.5 |  | 0.00059814 | Sm3air / mdepth*m2tot diff area*min
4 | 9” Ceramic Disc |  | 0.40149 | 0.0373 | 0.6 | 6 | estimated design aSOTE | 16.4434 | %
5 | 9” EPDM Membrane Disc |  | 0.28309 | 0.0263 | 0.5 | 2.5 | estimated O2 transferred (OTRtr) | 69492.9729 | lbO2/day
6 | 12” Square Ceramic Plate |  | 0.99997 | 0.0929 | 3 | 12 |  | 31549.8097 | kgO2/day
7 | 14” Ceramic Disc |  | 0.92139 | 0.0856 | 1.5 | 12 | DO2 (OTRtr - OTRreq) | 6062.1029 | lbO2/day
8 | 14” EPDM Membrane Disc |  | 0.68458 | 0.0636 | 2 | 6 |  | 2752.1947 | kgO2/day
9 | Ceramic Tube |  | 1.3003 | 0.1208 | 0.5 | 8 |  | DESIGN aSOTE PROBABLY UNDERESTIMATED
10 | EPDM Membrane Tube 2" X 3' |  | 1.57 | 0.14586 | 1 | 5 | OPERATING RANGES
11 | Large EPDM Tube 3" x 5' |  | 3.92 | 0.36418 | 3 | 12
12 | Plastic Tube |  | 1.1507 | 0.1069 | 1 | 5
13 | Polyurethane Tube 2" X 4' |  | 2.09 | 0.19417 | 1.5 | 6 | MIN operating AFR | 16508.5284 | SCFM
14 | PVC Membrane Tube |  | 0.86865 | 0.0807 | 1 | 5 | MAX operating AFR | 82542.6419 | SCFM
15 | Silicone Membrane Tube 2" X 4' |  | 1.9 | 0.17652 | 1.9 | 5.7
16 | Polyurethane Panel 4' x 11' |  | 44 | 4.0877 | 18 | 30 | MIN diffusers usable | 6604 | (@ max AFR/diff)
17 | Polyurethane Strip Panels 6" x 8' |  | 24 | 2.2297 | 20 | 35 | MAX diffusers usable | 33018 | (@ min AFR/diff)
18 | User defined - enter name |  | 0 | 0 | 0 | 0
19 | User defined - enter name |  | 0 | 0 | 0 | 0 | MIN normalized air flux | 0.11774 | Sft3air / ftdepth*ft2tot diff area*min
20 | User defined - enter name |  | 0 | 0 | 0 | 0 | MIN normalized air flux | 0.00059814 | Sm3air / mdepth*m2tot diff area*s
Enter diffuser code from above list | [6 empty] | MAX normalized air flux | 0.58869 | Sft3air / ftdepth*ft2tot diff area*min
Diffuser Code | Diffuser |  | Area |  | min AFR | max AFR | MAX normalized air flux | 0.0029905 | Sm3air / mdepth*m2tot diff area*s
|  |  | ft2 | m2 | SCFM/diff | SCFM/diff
Diffuser Code | Diffuser |  |  | Area | min AFR | max AFR
5 | 9” EPDM Membrane Disc |  | 0.28309 | 0.086286 | 0.5 | 2.5 | MIN estimated aSOTE (@max AFR/diff) | 12.4476 | %
[7 empty] | MAX estimated aSOTE (@min AFR/diff) | 16.4434 | %
Insert diffuser data in the green cells:
design aSOTE | 15 | % |  |  |  |  | MIN O2 transferable (OTRtr) | 52605.7315 | lbO2/day
diffuser depth | 15 | ft | [5 empty] | 23883.0021 | kgO2/day
| 4.572 | m |  |  |  |  | MAX O2 transferable (OTRtr) | 69492.9729 | lbO2/day
operating AFR/diffuser | 0.5 | SCFM/diff | [5 empty] | 31549.8097 | kgO2/day
design DWP | 20 | inH2O
ECONOMIC DATA | [6 empty] | AIR FLOW BEFORE CLEANING
Diffuser name | [6 empty] | Air Flow Rate | 41073.5283 | SCFM
[8 empty] | 1163.0728 | Sm3air / min
[7 empty] | DAFR | 24564.9999 | SCFM
[8 empty] | 695.6033 | Sm3air / min
[7 empty] | AFR increase during operating period | 148.8019 | %
Years in service |  | 2
Yearly maintenance cost [$] |  | 0 |  |  |  |  | CLEANING FREQUENCY
Cleaning cost [$] |  | 10000
Design aSOTE [%] |  | 15
Yearly efficiency loss DaSOTE/yr [%/yr] |  | 5 |  |  |  |  | Diffuser name |  | 9” EPDM Membrane Disc
aSOTE before cleaning [%] |  | 5 |  |  |  |  | Service period [yrs] |  | 2
Annual interest rate [%] |  | 4% |  |  |  |  | Time between cleaning events [mo] |  | 5
Power cost [$/kWh] |  | 0.065 |  |  |  |  | Net Present Value of power cost [$] |  | 688291.0398
Yearly increase in DWP [inH2O/yr] |  | 5 |  |  |  |  | Net Present Value of membrane cleaning cost [$] |  | 10000
DWP before cleaning [inH2O] |  | 30 |  |  |  |  | Net Present Value of Dpower [$] |  | 40839.3545
Fouling factor F |  | 0.33333 |  |  |  |  | Net Present Value of net loss [$] |  | 30839.3545
Pressure factor Y |  | 1.5 |  |  |  |  | Total present worth [$] |  | 0

## Economic Analysis (hidden)
NPV COSTS | [11 empty] | INITIAL PARAMETERS
capital cost |  |  | 0 | [8 empty] | Airflow rate initial | 1000 | SFCM
power cost |  |  | 688291.0398 | [8 empty] | aSOTE initial | 15% | %
Dpower cost |  |  | 40839.3545 | [8 empty] | aSOTE final | 5% | %
cleaning cost |  |  | 10000 | [8 empty] | Discharge P initial | 20 | inH2O
maintenance cost |  |  | 0 | [8 empty] | time in operation | 2 | yrs
Present Worth |  |  | 0
UNIT COSTS | [11 empty] | Defficiency / yr | 5% | %
cleaning cost |  |  | 10000 | [8 empty] | Defficiency / mo | 0.4074% | %
annual interest rate |  |  | 4% | [8 empty] | Defficiency / yr | 5% | %
power cost |  |  | 0.065 | [8 empty] | Defficiency / mo | 0.4074% | %
Power Es |  |  | 0
Labor Es |  |  | 0
Membrane Es |  |  | 0
CASH FLOWS
Mo |  | Capital | Power base | Power | Power Loss factor | Cum Power | months of op. | DPower | Sum of Loss | Cumulative energy wasted | DPower to Cleaning factor | Power to Cleaning ratio | Cleaning cost | Cleaning
0 | Jan | 0 | 35717.2941 | 35717.2941 | 1 | 35717.2941 | 1 | 0 | 0 | 0 | 0 | 0.023331 | 10000 | 0
1 | Feb | 0 | 35717.2941 | 37150.977 | 1.0401 | 72868.2711 | 2 | 1433.6829 | 1433.6829 | 0 | 0 | 0.023331 | 10000 | 0
2 | Mar | 0 | 35717.2941 | 38668.7452 | 1.0826 | 111537.0164 | 3 | 2951.4511 | 4385.134 | 1433.6829 | 0.14337 | 0.023331 | 10000 | 0
3 | Apr | 0 | 35717.2941 | 40278.25 | 1.1277 | 151815.2663 | 4 | 4560.9559 | 8946.0899 | 4385.134 | 0.43851 | 0.023331 | 10000 | 0
4 | May | 0 | 35717.2941 | 41988.0986 | 1.1756 | 193803.365 | 5 | 6270.8045 | 15216.8944 | 8946.0899 | 0.89461 | 0.023331 | 10000 | 0
5 | Jun | 0 | 35717.2941 | 35717.2941 | 1 | 219520.6591 | 1 | 0 | 15216.8944 | 5216.8944 | 0.52169 | 0.023331 | 10000 | 10000
6 | Jul | 0 | 35717.2941 | 37150.977 | 1.0401 | 266671.6361 | 2 | 1433.6829 | 16650.5773 | 5216.8944 | 0.52169 | 0.023331 | 10000 | 0
7 | Aug | 0 | 35717.2941 | 38668.7452 | 1.0826 | 305340.3813 | 3 | 2951.4511 | 19602.0284 | 6650.5773 | 0.66506 | 0.023331 | 10000 | 0
8 | Sep | 0 | 35717.2941 | 40278.25 | 1.1277 | 345618.6313 | 4 | 4560.9559 | 24162.9842 | 9602.0284 | 0.9602 | 0.023331 | 10000 | 0
9 | Oct | 0 | 35717.2941 | 35717.2941 | 1 | 361335.9254 | 1 | 0 | 24162.9842 | 4162.9842 | 0.4163 | 0.023331 | 10000 | 10000
10 | Nov | 0 | 35717.2941 | 37150.977 | 1.0401 | 418486.9024 | 2 | 1433.6829 | 25596.6671 | 4162.9842 | 0.4163 | 0.023331 | 10000 | 0
11 | Dec | 0 | 35717.2941 | 38668.7452 | 1.0826 | 457155.6477 | 3 | 2951.4511 | 28548.1182 | 5596.6671 | 0.55967 | 0.023331 | 10000 | 0
12 | Jan | 0 | 35717.2941 | 40278.25 | 1.1277 | 497433.8977 | 4 | 4560.9559 | 33109.0741 | 8548.1182 | 0.85481 | 0.023331 | 10000 | 0
13 | Feb | 0 | 35717.2941 | 35717.2941 | 1 | 503151.1918 | 1 | 0 | 33109.0741 | 3109.0741 | 0.31091 | 0.023331 | 10000 | 10000
14 | Mar | 0 | 35717.2941 | 37150.977 | 1.0401 | 570302.1688 | 2 | 1433.6829 | 34542.757 | 3109.0741 | 0.31091 | 0.023331 | 10000 | 0
15 | Apr | 0 | 35717.2941 | 38668.7452 | 1.0826 | 608970.914 | 3 | 2951.4511 | 37494.2081 | 4542.757 | 0.45428 | 0.023331 | 10000 | 0
16 | May | 0 | 35717.2941 | 40278.25 | 1.1277 | 649249.164 | 4 | 4560.9559 | 42055.164 | 7494.2081 | 0.74942 | 0.023331 | 10000 | 0
17 | Jun | 0 | 35717.2941 | 35717.2941 | 1 | 644966.4581 | 1 | 0 | 42055.164 | 2055.164 | 0.20552 | 0.023331 | 10000 | 10000
18 | Jul | 0 | 35717.2941 | 37150.977 | 1.0401 | 722117.4351 | 2 | 1433.6829 | 43488.8468 | 2055.164 | 0.20552 | 0.023331 | 10000 | 0
19 | Aug | 0 | 35717.2941 | 38668.7452 | 1.0826 | 760786.1804 | 3 | 2951.4511 | 46440.298 | 3488.8468 | 0.34888 | 0.023331 | 10000 | 0
20 | Sep | 0 | 35717.2941 | 40278.25 | 1.1277 | 801064.4303 | 4 | 4560.9559 | 51001.2538 | 6440.298 | 0.64403 | 0.023331 | 10000 | 0
21 | Oct | 0 | 35717.2941 | 35717.2941 | 1 | 786781.7245 | 1 | 0 | 51001.2538 | 1001.2538 | 0.10013 | 0.023331 | 10000 | 10000
22 | Nov | 0 | 35717.2941 | 37150.977 | 1.0401 | 873932.7014 | 2 | 1433.6829 | 52434.9367 | 1001.2538 | 0.10013 | 0.023331 | 10000 | 0
23 | Dec | 0 | 35717.2941 | 38668.7452 | 1.0826 | 912601.4467 | 3 | 2951.4511 | 55386.3878 | 2434.9367 | 0.24349 | 0.023331 | 10000 | 0
24 | Jan | 0 | 35717.2941 | 40278.25 | 1.1277 | 952879.6967 | 4 | 4560.9559 | 59947.3437 | 5386.3878 | 0.53864 | 0.023331 | 10000 | 0
25 | Feb | 0 | 35717.2941 | 41988.0986 | 1.1756 | 994867.7953 | 5 | 6270.8045 | 66218.1482 | 9947.3437 | 0.99473 | 0.023331 | 10000 | 0
26 | Mar | 0 | 35717.2941 | 35717.2941 | 1 | 970585.0894 | 1 | 0 | 66218.1482 | 6218.1482 | 0.62181 | 0.023331 | 10000 | 10000
27 | Apr | 0 | 35717.2941 | 37150.977 | 1.0401 | 1067736.0664 | 2 | 1433.6829 | 67651.8311 | 6218.1482 | 0.62181 | 0.023331 | 10000 | 0
28 | May | 0 | 35717.2941 | 38668.7452 | 1.0826 | 1106404.8117 | 3 | 2951.4511 | 70603.2822 | 7651.8311 | 0.76518 | 0.023331 | 10000 | 0
NPV |  | 0 |  | 647451.6853 |  |  |  | 40839.3545 | 67887.7714 |  |  |  | 169837.1463
POWER CALCULATIONS
|  | Air GASFlow | Air MASSflow | Inlet P | Discharge P |  | Discharge P | DWP increase | Total P | Inlet Temp | blower+motor | Power | Power | Kwh Cost | Monthly Power
Mo | Mo | (SCFM) | (lb/sec) | (psia) | (in Hg) |  | (psia) | (psia) | (psia) | (deg F) | efficiency | HP | kW | (USD) | Cost
0 | Jan | 16508.5284 | 20.6357 | 14.2 | 20 |  | 24.5262 | 0 | 24.5262 | 68 | 0.61 | 1023.043 | 763.19 | 0.065 | 35717.2941
1 | Feb | 16980.2006 | 21.2253 | 14.2 | 20.0815 |  | 24.5662 | 0.099923 | 24.6662 | 68 | 0.61 | 1064.1076 | 793.8243 | 0.065 | 37150.977
2 | Mar | 17479.6183 | 21.8495 | 14.2 | 20.1633 |  | 24.6064 | 0.20017 | 24.8066 | 68 | 0.61 | 1107.5808 | 826.2552 | 0.065 | 38668.7452
3 | Apr | 18009.3037 | 22.5116 | 14.2 | 20.2454 |  | 24.6468 | 0.30075 | 24.9475 | 68 | 0.61 | 1153.6815 | 860.6464 | 0.065 | 40278.25
4 | May | 18572.0944 | 23.2151 | 14.2 | 20.3279 |  | 24.6873 | 0.40166 | 25.089 | 68 | 0.61 | 1202.6563 | 897.1816 | 0.065 | 41988.0986
5 | Jun | 19171.1943 | 23.964 | 14.2 | 20.4107 |  | 24.728 | 0.5029 | 25.2309 | 68 | 0.61 | 1254.7836 | 936.0686 | 0.065 | 43808.0092
6 | Jul | 19810.2341 | 24.7628 | 14.2 | 20.4939 |  | 24.7689 | 0.60447 | 25.3733 | 68 | 0.61 | 1310.3789 | 977.5426 | 0.065 | 45748.9954
7 | Aug | 20493.3456 | 25.6167 | 14.2 | 20.5774 |  | 24.8099 | 0.70638 | 25.5163 | 68 | 0.61 | 1369.801 | 1021.8716 | 0.065 | 47823.59
8 | Sep | 21225.2508 | 26.5316 | 14.2 | 20.6612 |  | 24.8511 | 0.80863 | 25.6597 | 68 | 0.61 | 1433.4604 | 1069.3615 | 0.065 | 50046.1159
9 | Oct | 22011.3712 | 27.5142 | 14.2 | 20.7454 |  | 24.8924 | 0.91122 | 25.8036 | 68 | 0.61 | 1501.8279 | 1120.3636 | 0.065 | 52433.0182
10 | Nov | 22857.9624 | 28.5725 | 14.2 | 20.8299 |  | 24.934 | 1.0141 | 25.9481 | 68 | 0.61 | 1575.4472 | 1175.2836 | 0.065 | 55003.2717
11 | Dec | 23772.2809 | 29.7154 | 14.2 | 20.9148 |  | 24.9756 | 1.1174 | 26.0931 | 68 | 0.61 | 1654.9485 | 1234.5916 | 0.065 | 57778.887
12 | Jan | 24762.7926 | 30.9535 | 14.2 | 21 |  | 25.0175 | 1.221 | 26.2386 | 68 | 0.61 | 1741.0676 | 1298.8364 | 0.065 | 60785.5434
13 | Feb | 25839.4357 | 32.2993 | 14.2 | 21.0856 |  | 25.0595 | 1.325 | 26.3846 | 68 | 0.61 | 1834.6677 | 1368.6621 | 0.065 | 64053.3859
14 | Mar | 27013.9555 | 33.7674 | 14.2 | 21.1715 |  | 25.1018 | 1.4293 | 26.5311 | 68 | 0.61 | 1936.7693 | 1444.8299 | 0.065 | 67618.0401
15 | Apr | 28300.3344 | 35.3754 | 14.2 | 21.2577 |  | 25.1441 | 1.534 | 26.6781 | 68 | 0.61 | 2048.5873 | 1528.2461 | 0.065 | 71521.9178
16 | May | 29715.3511 | 37.1442 | 14.2 | 21.3443 |  | 25.1867 | 1.639 | 26.8257 | 68 | 0.61 | 2171.5793 | 1619.9981 | 0.065 | 75815.9128
17 | Jun | 31279.3169 | 39.0991 | 14.2 | 21.4313 |  | 25.2294 | 1.7444 | 26.9738 | 68 | 0.61 | 2307.5099 | 1721.4024 | 0.065 | 80561.6332
18 | Jul | 33017.0568 | 41.2713 | 14.2 | 21.5186 |  | 25.2723 | 1.8502 | 27.1225 | 68 | 0.61 | 2458.5361 | 1834.0679 | 0.065 | 85834.378
19 | Aug | 34959.2366 | 43.699 | 14.2 | 21.6063 |  | 25.3154 | 1.9563 | 27.2717 | 68 | 0.61 | 2627.3219 | 1959.9821 | 0.065 | 91727.1633
20 | Sep | 37144.1889 | 46.4302 | 14.2 | 21.6943 |  | 25.3586 | 2.0628 | 27.4214 | 68 | 0.61 | 2817.1977 | 2101.6295 | 0.065 | 98356.2591
21 | Oct | 39620.4681 | 49.5256 | 14.2 | 21.7827 |  | 25.4021 | 2.1696 | 27.5716 | 68 | 0.61 | 3032.3818 | 2262.1569 | 0.065 | 105868.9408
22 | Nov | 42450.5016 | 53.0631 | 14.2 | 21.8714 |  | 25.4457 | 2.2768 | 27.7225 | 68 | 0.61 | 3278.298 | 2445.6103 | 0.065 | 114454.5623
23 | Dec | 45715.9248 | 57.1449 | 14.2 | 21.9605 |  | 25.4894 | 2.3844 | 27.8738 | 68 | 0.61 | 3562.0386 | 2657.2808 | 0.065 | 124360.7401
24 | Jan | 49525.5852 | 61.907 | 14.2 | 22.05 |  | 25.5334 | 2.4923 | 28.0257 | 68 | 0.61 | 3893.0601 | 2904.2228 | 0.065 | 135917.6293
25 | Feb | 54027.9111 | 67.5349 | 14.2 | 22.1398 |  | 25.5775 | 2.6007 | 28.1782 | 68 | 0.61 | 4284.258 | 3196.0564 | 0.065 | 149575.4414
26 | Mar | 59430.7022 | 74.2884 | 14.2 | 22.23 |  | 25.6218 | 2.7094 | 28.3312 | 68 | 0.61 | 4753.6855 | 3546.2494 | 0.065 | 165964.4723
27 | Apr | 66034.1136 | 82.5426 | 14.2 | 22.3206 |  | 25.6663 | 2.8184 | 28.4848 | 68 | 0.61 | 5327.42 | 3974.2553 | 0.065 | 185995.1495
28 | May | 74288.3778 | 92.8605 | 14.2 | 22.4115 |  | 25.711 | 2.9279 | 28.6389 | 68 | 0.61 | 6044.5772 | 4509.2546 | 0.065 | 211033.1135
AIR FLOW RATE CALCULATIONS
Mo | Mo | aSOTE (%) | DO | Beta | C star |  | OTE (%) | Airflow rate (SCFM)
0 | Jan | 15 | 2 | 0.99 | 10.75 |  | 12.0593 | 16508.5284
1 | Feb | 14.5833 | 2 | 0.99 | 10.75 |  | 11.7243 | 16980.2006
2 | Mar | 14.1667 | 2 | 0.99 | 10.75 |  | 11.3893 | 17479.6183
3 | Apr | 13.75 | 2 | 0.99 | 10.75 |  | 11.0544 | 18009.3037
4 | May | 13.3333 | 2 | 0.99 | 10.75 |  | 10.7194 | 18572.0944
5 | Jun | 12.9167 | 2 | 0.99 | 10.75 |  | 10.3844 | 19171.1943
6 | Jul | 12.5 | 2 | 0.99 | 10.75 |  | 10.0494 | 19810.2341
7 | Aug | 12.0833 | 2 | 0.99 | 10.75 |  | 9.7144 | 20493.3456
8 | Sep | 11.6667 | 2 | 0.99 | 10.75 |  | 9.3795 | 21225.2508
9 | Oct | 11.25 | 2 | 0.99 | 10.75 |  | 9.0445 | 22011.3712
10 | Nov | 10.8333 | 2 | 0.99 | 10.75 |  | 8.7095 | 22857.9624
11 | Dec | 10.4167 | 2 | 0.99 | 10.75 |  | 8.3745 | 23772.2809
12 | Jan | 10 | 2 | 0.99 | 10.75 |  | 8.0395 | 24762.7926
13 | Feb | 9.5833 | 2 | 0.99 | 10.75 |  | 7.7046 | 25839.4357
14 | Mar | 9.1667 | 2 | 0.99 | 10.75 |  | 7.3696 | 27013.9555
15 | Apr | 8.75 | 2 | 0.99 | 10.75 |  | 7.0346 | 28300.3344
16 | May | 8.3333 | 2 | 0.99 | 10.75 |  | 6.6996 | 29715.3511
17 | Jun | 7.9167 | 2 | 0.99 | 10.75 |  | 6.3646 | 31279.3169
18 | Jul | 7.5 | 2 | 0.99 | 10.75 |  | 6.0297 | 33017.0568
19 | Aug | 7.0833 | 2 | 0.99 | 10.75 |  | 5.6947 | 34959.2366
20 | Sep | 6.6667 | 2 | 0.99 | 10.75 |  | 5.3597 | 37144.1889
21 | Oct | 6.25 | 2 | 0.99 | 10.75 |  | 5.0247 | 39620.4681
22 | Nov | 5.8333 | 2 | 0.99 | 10.75 |  | 4.6897 | 42450.5016
23 | Dec | 5.4167 | 2 | 0.99 | 10.75 |  | 4.3547 | 45715.9248
24 | Jan | 5 | 2 | 0.99 | 10.75 |  | 4.0198 | 49525.5852
25 | Feb | 4.5833 | 2 | 0.99 | 10.75 |  | 3.6848 | 54027.9111
26 | Mar | 4.1667 | 2 | 0.99 | 10.75 |  | 3.3498 | 59430.7022
27 | Apr | 3.75 | 2 | 0.99 | 10.75 |  | 3.0148 | 66034.1136
28 | May | 3.3333 | 2 | 0.99 | 10.75 |  | 2.6798 | 74288.3778