## Sheet1
Energy Savings Estimation Worksheet for Night Setback
Building Name: | [7 empty] | Location (city) |  |  |  |  | ECM No.
ECM Description:
Instructions
| Complete this form for each building where the winter Occupied Temperature will be reduced. | [8 empty] | Conversion Factors (CF)
| a) Complete the input assumptions and provide: | [8 empty] | to | Conversion | Units
| - a cost estimate for the proposed option. | [8 empty] | Electric | 293 | kWh/mmBtu
| b) The spreadsheet will calculate the savings for you. | [8 empty] | Natural Gas | 10 | Therms/mmBtu
[10 empty] | Natural Gas | 971 | Cubic feet/mmBtu
[10 empty] | #2 oil | 7.2 | Gallons/mmBtu
[10 empty] | #6 oil | 6.7 | Gallons/mmBtu
[10 empty] | Propane | 10.5 | Gallons/mmBtu
Input Assumptions
| 1) Floor Area………………………………………………………………………. |  |  | (FA) | 1000 | Square Feet |  | 6) Average Winter Outdoor Temperature……………………………………… |  |  |  |  | (AWT) | 39 | ºF
| 2) Unoccupied hours per day………………………………………………………. |  |  | (HPD) | 24 | Hours/Day |  | 7) Average Energy Cost Heating Fuel (e.g. kWh, Gal., therms)…….. |  |  |  |  | (AEC) | 0.063 | / | kWh
(heating unit)
| 3) Heating Degree Days for the site……………………………………………. |  |  | (HDD) | 400 |  |  | 8) Estimated Heating System Efficiency**……………………………………. |  |  |  |  | (HSE) | 100%
| 4) Current Unoccupied Heating Setpoint…………………………………………………….. |  |  | (CUHS) | 72 | ºF |  | 9) Estimated Project Cost………………………………………………………… |  |  |  |  | (PC) | 0
| 5) Proposed Unoccupied Heating Setpoint………………………………………………….. |  |  | (PUHS) | 45 | ºF | 10) Conversion Factor………………………………………………….. | [5 empty] | (CF) | 293 |  | kWh
(Units)
Notes: * The value 0.198 is the estimated U-Factor (which is one over the total R-Value) for the walls and roof, and an adjustment to account for the wall area and assumes a square building and correction factor.
** The "estimated heating system efficiency" is the annual heating system efficiency; for gas or oil heat use 0.7, for electric resistance heat use 1.0, for heat pumps use 2.0.
A
| Building Heat Loss = |  | 0.198* x | 1000 | x | 24 |  | x |  | 400 | / 1,000,000 = | 1.9008 | mmBtu/year
|  |  |  | (FA) |  | (HPD) |  |  |  | (HDD)
B
| Total heat used = |  | 1.9008 | / |  | 100% |  |  |  |  | = | 1.9008 | mmBtu/year
|  |  | (A) |  |  | (HSE)
C
| Existing Heating Energy Consumption = |  |  | 1.9008 | x | 293 |  | kWh | /mmBtu |  | = | 556.9344 | kWh | /year
|  |  |  | (B) |  | (CF) |  | (Units) |  |  |  |  | (Heating Units/year)
D
|  | 72 | - | 39 | - | 27 |  |  |  |  | = | 6
|  | (CUHS) |  | (AWT) |  | (CUHS - PUHS)
E
|  | 6 | / ( | 72 | - | 39 | ) |  |  |  | = | 0.18182
|  | (D) |  | (CUHS) |  | (AWT)
F
| Future Heating Energy Consumption = |  |  | 0.18182 | x | 556.9344 |  |  |  |  | = | 101.2608 | kWh | /year
|  |  |  | (E) |  | (C) | [6 empty] | (Heating Units)
G
| Estimated Energy Savings |  | = | 556.9344 | - | 101.2608 |  |  |  |  | = | 455.6736 | kWh | /year
|  |  |  | (C) |  | (F) | [6 empty] | (Heating Units) | nits)
| Dollar Savings = |  | 455.6736 | x | 0.063 | = |  | 28.7074 | $/year
|  |  | (G) |  | (AEC)