Spring Break Shutdown Activities

Facility Name: ________________________________________________________________

C - Custodian: _______________________	A - Administration Staff: ____________________

M - Maint. Staff: _____________________ 	R - Res. Conserv. Spec.: _____________________

K - Kitchen Staff: _____________________

Note:  Fill in the above spaces with responsible staff.  Indicate below in the box which staff will be responsible for getting individual tasks completed.

Lighting

Turn off as many exterior lights as permitted by the administration.  Leave only security lighting.  Set up a new schedule on the time clocks for the exterior lighting if appropriate.

Implement an all-dark campus for interior and exterior lights if permitted by the administration.

Ensure all exterior lighting that is left on is controlled by a photocell or time clock with proper settings.

Use interior lighting only in the areas being occupied.  Use daylighting if adequate.

Turn off display lighting.

HVAC

Set HVAC time clocks and/or EMCS for minimum operating time.  Operation should match the Spring occupancy levels.

Set HVAC controls/switches to allow in the amount of outside air (OSA) needed for the number of occupants scheduled for the different areas (caution: if solvents or other odor-

causing agents are used, maintain OSA if necessary for proper indoor air quality (IAQ)).

Set HVAC controls to a minimum temperature of 55 degrees F during times when not occupied.

If cooling is available, set HVAC controls to a minimum of 78 degrees F for cooling during times when occupied.

Turn off all automatic and manually operated exhaust fans.  Study the need for ventilation fans during the set back period.  Turn off those that do not interfere with the HVAC system.

Domestic Water and Domestic Hot Water (DHW)

Turn off electric water heaters at the circuit box (if not needed over the break).  Turn off any hot water boosters for kitchen dishwashers.

Turn off DHW circulation pumps, if feasible.

Turn off automatic urinal flushing systems.

Check actual water meters to verify there is no use due to water leaks.

Envelope

Close all curtains/blinds in unoccupied areas to help reduce building heat gain/loss.

Kitchen

Confirm that all kitchen equipment (gas and electric) is turned off.  For equipment that has a pilot light and is not used during the spring, the gas valves should be closed.

Consolidate items from multiple refrigerators into one, and turn the others off.

Miscellaneous Equipment

Turn off compressors used in shops (auto, wood, etc.)

Check to make sure all unnecessary electric appliances (copiers, computers, printers, TVs, fax, radios water coolers, task lighting, etc.) are turned off.

Make sure breakroom refrigerators (and individual units) are cleaned out and turned off, if possible.

Unplug vending machines (inform vendors of intentions).

Garbage

Discontinue unneeded garbage services.