###### BUILDING SYSTEMS COMMISSIONING CHECKLIST

The following list provides potential systems that could require commissioning.

1.0		AIR DISTRIBUTION:

The Commissioning Agent (CA) will verify and report on the operation and accessibility of the following items.

1.1	EQUIPMENT:

____	Air filtration, dampers, diffusers, grilles, fire dampers and access doors.

____	Hoods and exhaust systems.

____	Heat buildup or noise in motor or shaft bearings.

____	Humidification equipment.

1.2	BALANCING:

Perform balancing for the following devices:

____	Motor current draw.  Compare running current to nameplate full load amps rating.

____	Motor starter contactor size and overload heater size.

____	Voltage and rotation of each motor driven fan or air handling device.

____	Belt tension and drive alignment.

____	Airflow at outlets with the thermostat adjusted to simulate full cooling, full heating, hood operation, etc. where appropriate.

____	Airflow at each air handler at simulated full cooling and/or maximum fresh air.

____	Airflow at each fume hood based on sash positions.

____	Air flow at each range, dishwasher and process hood.

____	Room static pressure with respect to adjacent spaces and outdoors.

____	Outside air rate into system.

____	Drafts or noise from air distribution devices.

2.0	PLUMBING AND PIPING SYSTEMS:

The CA will verify and report on the operation and accessibility of the following items.

2.1	EQUIPMENT

____	Sewage lift pump.

____	Sump pumps.

____	Chemical feed equipment.

____	Air compressor, de-ionized water equipment and other process equipment.

____	Pump motor current draw.  Compare running current to nameplate full load amps rating.  Overload heater size.

2.2	PIPING

____	Strainers, valves, fixtures, steam traps, air purge, and blow down systems, and instrumentation and flow measuring or control.  Bypass and shut off valves for maintenance.

____	Cleaning, degreasing and flushing of piping systems.

____	Fluid temperatures and pressures.

____	Fuel supply system.  Check for water in fuel.

____	Test ports for temperature, pressure and chemical treatment measurements.

2.3	WATER AND STEAM TREATMENT

____	Filling of hydronic and chilled water systems.

____	Glycol concentration and pH.

____	Specific conductance.

____	Total alkalinity.

____	Suspended solids.

____	Silica.

____	Additives for steam system and protection of the condensate piping.

____	Chemical or additive injection systems.

3.0	HEATING AND COOLING:

3.1	PLANT EQUIPMENT:

The CA will verify and report on the operation and accessibility of the following items.

____	Service access.

____	Compressors.

____	Chillers.

____	Boilers.

____	Cooling towers.

____	Combustion air and exhaust systems.

____	Safety devices and controls.

4.0	CONTROL SYSTEMS:

The CA will verify and report on the operation and accessibility of the following items.

____	Functioning of each control program.

____	Functioning of each hardware control point.

____	Instruction and training for Owner's operating personnel in the proper operation of the systems.  The balancing contractor will correct flows and assist in fine tuning system.

____	Functioning of following devices:

____	Thermostats and temperature sensors,

____	Automatic dampers and valves,

____	Fresh air and return air dampers,

____	Economizer operation,

____	Air handler, boiler, chiller and pump starting and stopping from program control,

____	Exhaust fan and air handler start and stop,

____	Variable air volume control of VAV air handlers, and tracking of associated return fan,

____	Surge and transient protection,

____	Freeze prevention control,

____	Labeling of each control device.

____	Function of control loops

____	Time schedules,

____	Optimum start/stop,

____	Reset type schedules,

____	Demand limiting,

____	Alarm sequences,

____	Maintenance alarms,

____	Remote communication (modem),

____	Low (or high) limits, and

____	Other system programming features.

____	Safety devices.

____	Instrumentation, gauges, thermometers, flow measuring devices.

____	Shutdown of air handling systems in the event of presence of smoke or products of combustion.

5.0	ELECTRICAL:

The CA will verify and report on the operation and accessibility of the following items.  Use NETA testing procedures where applicable.

____	Circuit breakers, and protective relays.

____	Low voltage circuit breakers, motor starters, motor controls,

____	Setpoints, sensitivity and location of lighting controls.

____	Equipment ground fault interruption devices.

____	Emergency power systems.

____	Fire alarm system.

____	Communication systems including, but not limited to, telephones, television, intercoms, local area networks (when included in the project).

Commissioning Certificate of Completion

Project No.	___________________					Date ___________________

Project Title	_____________________________________________________________________

Building	_____________________________________________________________________

Address	_____________________________________________________________________

Contractors providing the following services for this project:

Mechanical	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

Electrical	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

Plumbing	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

Sheet Metal	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

Balancing	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

Commissioning Certificate of Completion

Controls	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

Fire Protection	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

Elevator	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

other		_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

The Commissioning Agent has observed the commissioning process and acknowledges that it was carried out according to the contract documents.

Commissioning	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date

The Client Agency acknowledges receipt of the following documents and services:

- Operating and Maintenance Manuals

- As-Built Drawings

- All certificates

- Operator instruction

Client Agency	_____________________________________________________________________

firm name

_____________________________________________________________________

signature					title			date