## Slide 1: Aeration System Opportunities
Aeration System Opportunities
Dave Reardon, PE, ENV SP HDR National Director - Water Sustainability
WW/W Sustainable Energy Cohort-Session 5
January 31, 2013

## Slide 2: All Set for an Hour Discussion of Fine Bubble Diffusers, Turbo Blowers, and Dissolved Oxygen (DO) Control?
Too Bad…
You Will Be Disappointed

## Slide 3: Presentation Agenda
Loading to Aeration Basin
Blowers
Impacts of SRT and Selectors
Sidestream Treatment
Overdesign
Take Away Points
Blower Pressure, Ammonia Control, and ML Recycle

## Slide 4: Improving Primary Clarifier Performance Can Make A Difference
Improved hydraulics and baffling can increase suspended solids (SS) removal by 10%
SS = BOD = Energy in activated sludge process
What Would Happen if We Removed 95% of SS Prior to Aeration?

## Slide 5: Much Has Been Said About Turbo Blowers

## Slide 6: Blower Selection and Sizing is Critical
40
50
60
70
100
Isentropic Efficiency (%)
80
70
60
50
80
90
Capacity (%)
Positive Displacement with VFD
Multi-Stage
IGV Single-Stage
Single-Stage Dual-Point Control and High-Speed Turbo Blowers

## Slide 7: Make Alpha Work for You, Not Against You in Heavily Loaded Section of Aeration Basin
Mechanical Aeration or Coarse Bubble Have Better Transfer Efficiency?
Energy Saving Benefits of Denitrification - Rosso and Stenstrom (2007)
Tank Length (%)
0
20
40
60
80
100
0
50
100
150
200
250
Tank Length (feet)
α
0.6
0.5
0.4
0.3
0.2
Conventional Process
Process with Anoxic Selector
Anoxic Selector (α not defined)

## Slide 8: Impact of MCRT on Oxygen Transfer
Rosso and Stenstrom (2007)
Field Oxygen Transfer Efficiency (Fouled Diffusers)
Tank Length (m)
0
250
500
750
1,000
Tank Length (feet)
20.0
16.0
12.0
8.0
4.0
Conventional MCRT ~ 2 days
Nitrifying MCRT > 10 days
0
100
200
300

## Slide 9: What About Blower Header Operating Pressures?

## Slide 10: Modification of Dissolved Oxygen (DO) Control System to Include Ammonia Control
Blower Energy Reduction of 5 to 10% May Be Possible

## Slide 11: Configuration of Aeration Basins Can Reduce Mixed Liquor Recycle Energy
75% Reduction in Mixed Liquor Recycle Energy and Less Equipment
Primary Effluent
Single Pass
Aeration Basin
Mixed Liquor Recycle
Primary Effluent
“Folded” Basin
Mixed Liquor Recycle

## Slide 12: Side Stream Treatment (Digester Centrate or Filtrate) Has Energy Advantages
Sidestreams are a high source of ammonia
100% reduction in carbon source required
Small footprint
50% reduction in energy
Anammox Tower

## Slide 13: Right Sizing and Proper Selection of Equipment Produces Large Energy Savings

## Slide 14: We Don’t Need to Optimize Energy … We Have a Brand New Plant!

## Slide 15: You Have Just Been Asked to Design an Activated Sludge Aeration System

## Slide 16: Where is the Energy? Blowers!!

## Slide 17: Peaking Factors for Overdesigned Blower Systems
Avg Condition
Worst Case
Peak Factor
Yearly: Peak Day versus Average Day BOD
1.00
1.20
1.20
Diffuser Alpha (a)
0.55
0.39
1.40
Peak Day versus Average Day Ammonia
1.00
1.30
1.15
Diurnal: Maximum Hour versus Average BOD
1.00
2.00
2.00
Design Year 2025 versus current Loads
1.00
1.34
1.34
Ten States Standards versus Actual BOD Data
1.00
1.10
1.10
This doesn’t even include the safety factor for temperature!

## Slide 18: What’s the Bottom Line?
A total safety (or peaking) factor of 5.7!

## Slide 19: Blower Design Conditions
Average Flow Conditions Now
5,000 cfm Air Flow
Worst Case Future
28,500 cfm

## Slide 20: Three-Blower Installation Will Require 14,250 cfm Blowers
Blower No. 1
14,250 cfm
Blower No. 2
14,250 cfm
Standby Blower
14,250 cfm
28,500 cfm

## Slide 21: Multi-Stage Blower Has Surge Point at Approximately 50-60 Percent of Design Capacity
5,000
0
2
4
6
8
10
12
10,000
Flow (cfm)
15,000
Discharge Pressure (psi)
Surge: 7,100 cfm
Design: 14,250 cfm at 8 psi
0

## Slide 22: Unit Power Consumption on Multi-Stage Centrifugal Blowers Increases at Throttled Conditions
0
10
20
30
40
50
60
70
40
70
100
HP/1,000 cfm
Percent of Design Flow
Constant Discharge Pressure

## Slide 23: Blower Power Consumption
HP
Percent of Design Flow
50
100
150
200
250
75
100
680 F, 360 RH, 5000 SCFM Blower
25









Single Stage, Inlet Guide Vanes, Outlet Diffusion Vanes
Multi-Stage VFD
Multi-Stage, Inlet Throttling

High Speed Turbo Blower

## Slide 24: What Should You Do?
Blower No. 1
8,000 cfm
Blower No. 2
8,000 cfm
Blower No. 3
14,250 cfm
Blower No. 4
14,250 cfm
OR
Blower No. 1
8,000 cfm
Blower No. 2
14,250 cfm
Blower No. 3
14,250 cfm
Blower No. 4
14,250 cfm

## Slide 25: It’s Becoming Quite Fashionable to Combine Blower Types
14,250 cfm
14,250 cfm
8,000 cfm
8,000 cfm
Two Single-Stage
Two Multi-Stage

## Slide 26: Channel Aeration Overdesign is Common
5 cfm/foot channel

## Slide 27: Don’t Scrimp on Adding Equipment that Will Optimize Energy at Average Conditions
$2.3 Million
$100,000
250 hp Blower Capital Cost
Energy (20 years)

## Slide 28: Your Overdesign Repellant
Equipment operates at “worst case” conditions < 5 percent of the time
Most designs are specified to be efficient at worst case conditions
Equipment is often unstable, inefficient at average/minimum conditions

## Slide 29: Your Overdesign Repellant (cont’d)
Use “jockey” pumps, blowers for minimum, average conditions
Kick your consultant in the behind! Ask about operation without all the safety factors

## Slide 30: Your Take Away Points
Efficient aeration design is much more than blowers and fine bubble diffusers
Reduced loading on aeration basins
Conduct sustainability reviews of aeration systems and other processes
Overdesign must be avoided
Challenge Your Consultants!

## Slide 31: Aeration System Opportunities
Aeration System Opportunities
Dave Reardon, PE, ENV SP HDR National Director - Water Sustainability
(916) 817-4820 Dave.Reardon@hdrinc.com