## 97464975819_2023-06-07_Q&ARepor
Question
Report Generated: | 2023-06-20 10:04
Topic | Meeting ID | Actual Start Time | Actual Duration (minutes) | # Question
HVAC Building Operations and IAQ at Pandemic's "End" | 97464975819 | 2023-06-07 13:30 | 93 | 7
Question Details
# | Question | Asker Name | Asker Email | Answer | Question Time | Answered Time | Answer Name | Answer Email
1 | Why did natural gas use go up during the pandemic? I would think more ventilation = more electricity use. | Len Kannapell | len.kannapell@seattle.gov | We had to heat all of that cold outside air when we increased the ventilation rates, which is primarily done with natural gas. | 2023-06-07 14:18 | 2023-06-07 14:33 | Nicole Laky (she/her) - King County Metro Transit | nlaky@kingcounty.gov
2 | Any assessments on reduced HVAC service life by using MERV 13 filters in a system designed for MERV 8? | Anonymous Attendee |  | Yes, early on we had a consultant do a study of our HVAC systems and identify all of the places that would benefit from MERV 13 and be able to handle them. There was an increase in wear-and-tear but it was minor. | 2023-06-07 14:19 | 2023-06-07 14:37 | Nicole Laky (she/her) - King County Metro Transit | nlaky@kingcounty.gov
3 | How did you determine that the MERV 13 filters "improved" IAQ? | Selena O'Neal | soneal@adacounty.id.gov | We purchased a 3 band meter with the primary focus being pm2.5. During smoke events we performed random monitoring of spaces, classrooms, gyms, lunch rooms etc. We polled the outside of the building assuming a prevailing wind could modify findings and then compiled the results | 2023-06-07 14:19 | 2023-06-07 14:39 | Travis Bown | travis.bown@mead354.org
4 | Thanks, Nicole - if I have this correct, the increase in electricity use (to move the heated air, unless you have a dedicated outside air system (DOAS)) is much less than the increase in natural gas to heat all that air. | Len Kannapell | len.kannapell@seattle.gov | It is less, although there is still an increase in electricity use. Moving the air is much less energy-intensive than heating it. | 2023-06-07 14:38 | 2023-06-07 14:40 | Nicole Laky (she/her) - King County Metro Transit | nlaky@kingcounty.gov
5 | exactly - thank you | Len Kannapell | len.kannapell@seattle.gov |  | 2023-06-07 14:46
6 | Last question: If you had DOAS and an HRV, would that have reduced your increase in natural gas heating? Decoupling heating from ventilation is typically more efficient | Len Kannapell | len.kannapell@seattle.gov | Our remodeled facilites of similar size and occupancy that have the benefit of condensing 4 pipe DOAS units with HRV are running around a 47.3 EUI vs buildings that only had light HVAC upgrades still running in the mid 50's. Our new buildings where we started from scratch with the same design are running 41.3 weather normalized EUI. | 2023-06-07 14:49 | 2023-06-07 14:53 | Travis Bown | travis.bown@mead354.org
6 | Last question: If you had DOAS and an HRV, would that have reduced your increase in natural gas heating? Decoupling heating from ventilation is typically more efficient | Len Kannapell | len.kannapell@seattle.gov | live answered | 2023-06-07 14:49 | 2023-06-07 15:03 | Travis Bown | travis.bown@mead354.org
7 | thanks, Travis - new buildings make good use of DOAS, but I would think it is difficult/$$ to add DOAS to existing buildings, to achieve the same very good EUI (41.3) for new bldgs. | Len Kannapell | len.kannapell@seattle.gov | live answered | 2023-06-07 14:56 | 2023-06-07 15:03 | Travis Bown | travis.bown@mead354.org